## 108420p0
| MAKERCODE | CGRYCODE | NAME1 | NAME2 | DATE | MANUF_STOP | SPVER | FLA_FILE | FRO_FILE | REA_FILE | RIT_FILE | LEF_FILE | BOT_FILE | ETC_FILE | ASS_FLG | REF_AB&HZ50&COMP@QRT | REF_AB&HZ60&COMP@QRT | REF_AB&COMP@QRT | ACL_AB&HZ50@QKW | ACL_AB&HZ60@QKW | ACL_AB&MAX@QKW | ACL_AB&MIN@QKW | HTS_AB&HZ50@QKW | HTS_AB&HZ50&LOTMP@QKW | HTS_AB&HZ60@QKW | HTS_AB&HZ60&LOTMP@QKW | HTS_AB&MAX@QKW | HTS_AB&MIN@QKW | SA_Q&HZ50@M3M | SA_Q&HZ50&HIGH@M3M | SA_Q&HZ50&MID@M3M | SA_Q&HZ50&LOW@M3M | SA_Q&HZ60@M3M | SA_Q&HZ60&HIGH@M3M | SA_Q&HZ60&MID@M3M | SA_Q&HZ60&LOW@M3M | SP&HZ50@PA | SP&HZ60@PA | NOISE_PWL&HZ50&HIGH@DB | NOISE_PWL&HZ50&MID@DB | NOISE_PWL&HZ50&LOW@DB | NOISE_PWL&HZ60&HIGH@DB | NOISE_PWL&HZ60&MID@DB | NOISE_PWL&HZ60&LOW@DB | NOISE_PWL&ACL&HZ50@DB | NOISE_PWL&ACL&HZ60@DB | NOISE_PWL&HTS&HZ50@DB | NOISE_PWL&HTS&HZ60@DB | SIZE_W@MM | SIZE_D@MM | SIZE_H@MM | PRD_QA@WKG | PHASE@ES | VOLTAGE@EV | ELEC_OUT&HZ50&COMP@EKW | ELEC_OUT&HZ60&COMP@EKW | ELEC_OUT&COMP@EKW | ELEC_OUT&FAN@EKW | ELECONSUM&ACL&HZ50@EKW | ELECONSUM&ACL&HZ60@EKW | ELECONSUM&HTS&HZ50@EKW | ELECONSUM&HTS&HZ60@EKW | ELECONSUM&HTS&HZ50&LOTMP@EKW | ELECONSUM&HTS&HZ60&LOTMP@EKW | ELECONSUM&HZ50@EKW | ELECONSUM&HZ60@EKW | OPE_A&ACL&HZ50@EA | OPE_A&ACL&HZ60@EA | OPE_A&ACL&MAX@EA | OPE_A&HTS&HZ50@EA | OPE_A&HTS&HZ60@EA | OPE_A&HTS&MAX@EA | OPE_A&HT&HZ50@EA | OPE_A&HT&HZ60@EA | OPE_A&HZ50@EA | OPE_A&HZ50&HTER@EA | OPE_A&HZ60@EA | OPE_A&HZ60&HTER@EA | STRT_A&HZ50@EA | STRT_A&HZ60@EA | ELEC_EF&ACL&HZ50@EFF | ELEC_EF&ACL&HZ60@EFF | ELEC_EF&HTS&HZ50@EFF | ELEC_EF&HTS&HZ50&HTER@EFF | ELEC_EF&HTS&HZ60@EFF | ELEC_EF&HTS&HZ60&HTER@EFF | ELEC_EF&HT&HZ50@EFF | ELEC_EF&HT&HZ60@EFF | ELEC_EF&HZ50@EFF | ELEC_EF&HZ60@EFF | RA_CONNECT&IN&LOC@MM | RA_CONNECT&IN&SIZE_W@MM | RA_CONNECT&IN&SIZE_H@MM | SA_CONNECT&OUT&LOC&NO01@MM | SA_CONNECT&OUT&SIZE_P&NO01@MM | SA_CONNECT&OUT&LOC&NO02@MM | SA_CONNECT&OUT&SIZE_P&NO02@MM | SA_CONNECT&OUT&LOC&NO03@MM | SA_CONNECT&OUT&SIZE_P&NO03@MM | SA_CONNECT&OUT&LOC&NO04@MM | SA_CONNECT&OUT&SIZE_P&NO04@MM | SA_CONNECT&OUT&LOC&NO05@MM | SA_CONNECT&OUT&SIZE_W&NO05@MM | SA_CONNECT&OUT&SIZE_H&NO05@MM | OA_CONNECT&SIZE_P@MM | OA_CONNECT&SIZE_W@MM | OA_CONNECT&SIZE_H@MM | AIR_DBT&INDOR&ACL@THC | AIR_DBT&INDOR&HTS@THC | AIR_WBT&INDOR&ACL@THC | AIR_OST_DB&ACL@THC | AIR_OST_DB&HTS@THC | AIR_OST_DB&HTS&LOW@THC | AIR_OST_WB&ACL@THC | AIR_OST_WB&HTS@THC | AIR_OST_WB&HTS&LOW@THC | C_T&ACL&IN@THC | H_T&HTS&IN@THC | CDH_T&ACL&IN@THC | CDH_T&HTS&IN@THC | CD_T&IN@THC | CH_CONNECT&IN&LOC@MM | CH_CONNECT&OUT&LOC@MM | CD_CONNECT&IN&OUT&METH | CD_CONNECT&IN&LOC@MM | CD_CONNECT&OUT&LOC@MM | RL_CONNECT&IN&SIZE_P@MM | RL_CONNECT&IN&LOC@MM | RG_CONNECT&IN&SIZE_P@MM | RG_CONNECT&IN&LOC@MM | D_CONNECT&OUT&SIZE_P@ASIZ | D_CONNECT&OUT&LOC@MM | CH_PLS&HZ50@KPA | CH_PLS&HZ60@KPA | CDH_PLS&HZ50@KPA | CDH_PLS&HZ60@KPA | CD_PLS&HZ50@KPA | CD_PLS&HZ60@KPA | 3D_D_FILE | 製品情報
21 | 108420 | 50053003220070 | PEFY-P45MG9 | ビル用マルチ 天井埋込形室内機 | 2022/9/15 |  | 08 | 108420\5005300\pefy-p45_56mg9_1.dxf | 108420\5005300\pefy-p45_56mg9_2.dxf | 108420\5005300\pefy-p45_56mg9_3.dxf | 108420\5005300\pefy-p45_56mg9_4.dxf | 108420\5005300\pefy-p45_56mg9_5.dxf | 108420\5005300\pefy-p45_56mg9_6.dxf | [5 empty] | 4.5 | 4.5 |  |  | 5 |  | 5 |  |  |  |  | 14 |  | 10 |  | 14 |  | 10 | 100 | 100 | 57 |  | 51 | 57 |  | 51 |  |  |  |  | 745 | 900 | 380 | 39 | 1 | 200 |  |  |  | 0.08 | 0.19 | 0.22 | 0.17 | 0.2 |  |  |  |  | 0.97 | 1.12 |  | 0.86 | 1.01 | [19 empty] | -0.5/447.4/-192.8/90/0 | 600 | 340 | [8 empty] | 14.3/-452.6/-160.8/270/0 | 550 | 250 |  |  |  | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 6.35 | -406.5/-168.5/-178/180/0 | 12.7 | -415.6/-237.6/-235.8/180/0 | 25 | -402.2/5.4/-52.3/180/0 | [6 empty] | 108420\5005300\pefy-p45_56mg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317114
22 | 108420 | 50053003220070 | PEFY-P56MG9 | ビル用マルチ 天井埋込形室内機 | 2022/9/15 |  | 08 | 108420\5005300\pefy-p45_56mg9_1.dxf | 108420\5005300\pefy-p45_56mg9_2.dxf | 108420\5005300\pefy-p45_56mg9_3.dxf | 108420\5005300\pefy-p45_56mg9_4.dxf | 108420\5005300\pefy-p45_56mg9_5.dxf | 108420\5005300\pefy-p45_56mg9_6.dxf | [5 empty] | 5.6 | 5.6 |  |  | 6.3 |  | 6.3 |  |  |  |  | 14 |  | 10 |  | 14 |  | 10 | 100 | 100 | 57 |  | 52 | 57 |  | 52 |  |  |  |  | 745 | 900 | 380 | 39 | 1 | 200 |  |  |  | 0.08 | 0.19 | 0.22 | 0.17 | 0.2 |  |  |  |  | 0.97 | 1.12 |  | 0.86 | 1.01 | [19 empty] | -0.5/447.4/-192.8/90/0 | 600 | 340 | [8 empty] | 14.3/-452.6/-160.8/270/0 | 550 | 250 |  |  |  | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 6.35 | -406.5/-168.5/-178/180/0 | 12.7 | -415.6/-237.6/-235.8/180/0 | 25 | -402.2/5.4/-52.3/180/0 | [6 empty] | 108420\5005300\pefy-p45_56mg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317115
23 | 108420 | 50053003220070 | PEFY-P71MG9 | ビル用マルチ 天井埋込形室内機 | 2022/9/15 |  | 08 | 108420\5005300\pefy-p71mg9_1.dxf | 108420\5005300\pefy-p71mg9_2.dxf | 108420\5005300\pefy-p71mg9_3.dxf | 108420\5005300\pefy-p71mg9_4.dxf | 108420\5005300\pefy-p71mg9_5.dxf | 108420\5005300\pefy-p71mg9_6.dxf | [5 empty] | 7.1 | 7.1 |  |  | 8 |  | 8 |  |  |  |  | 19 |  | 13.5 |  | 19 |  | 13.5 | 100 | 100 | 61 |  | 56 | 61 |  | 56 |  |  |  |  | 745 | 900 | 380 | 40 | 1 | 200 |  |  |  | 0.1 | 0.24 | 0.28 | 0.22 | 0.26 |  |  |  |  | 1.23 | 1.42 |  | 1.12 | 1.31 | [19 empty] | -0.5/447.4/-192.8/90/0 | 600 | 340 | [8 empty] | 14.3/-452.6/-160.8/270/0 | 550 | 250 |  |  |  | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | -406.5/-168.5/-178/180/0 | 15.88 | -415.6/-237.6/-235.8/180/0 | 25 | -402.2/5.4/-52.3/180/0 | [6 empty] | 108420\5005300\pefy-p71mg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317116
24 | 108420 | 50053003220070 | PEFY-P80MG9 | ビル用マルチ 天井埋込形室内機 | 2022/9/15 |  | 08 | 108420\5005300\pefy-p80_90mg9_1.dxf | 108420\5005300\pefy-p80_90mg9_2.dxf | 108420\5005300\pefy-p80_90mg9_3.dxf | 108420\5005300\pefy-p80_90mg9_4.dxf | 108420\5005300\pefy-p80_90mg9_5.dxf | 108420\5005300\pefy-p80_90mg9_6.dxf | [5 empty] | 8 | 8 |  |  | 9 |  | 9 |  |  |  |  | 22 |  | 15.5 |  | 22 |  | 15.5 | 100 | 100 | 61 |  | 56 | 61 |  | 56 |  |  |  |  | 1030 | 900 | 380 | 51 | 1 | 200 |  |  |  | 0.11 | 0.28 | 0.31 | 0.26 | 0.29 |  |  |  |  | 1.44 | 1.58 |  | 1.33 | 1.47 | [19 empty] | -0.3/447.4/-191.8/90/0 | 885 | 340 | [8 empty] | 14.5/-452.6/-160.8/270/0 | 835 | 250 |  |  |  | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | -549.3/168.5/-178/180/0 | 15.88 | -558.4/-237.6/-235.8/180/0 | 25 | -545/5.4/-52.3/180/0 | [6 empty] | 108420\5005300\pefy-p80_90mg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317117
25 | 108420 | 50053003220070 | PEFY-P90MG9 | ビル用マルチ 天井埋込形室内機 | 2022/9/15 |  | 08 | 108420\5005300\pefy-p80_90mg9_1.dxf | 108420\5005300\pefy-p80_90mg9_2.dxf | 108420\5005300\pefy-p80_90mg9_3.dxf | 108420\5005300\pefy-p80_90mg9_4.dxf | 108420\5005300\pefy-p80_90mg9_5.dxf | 108420\5005300\pefy-p80_90mg9_6.dxf | [5 empty] | 9 | 9 |  |  | 10 |  | 10 |  |  |  |  | 25 |  | 18 |  | 25 |  | 18 | 100 | 100 | 63 |  | 58 | 63 |  | 58 |  |  |  |  | 1030 | 900 | 380 | 51 | 1 | 200 |  |  |  | 0.14 | 0.29 | 0.33 | 0.27 | 0.31 |  |  |  |  | 1.47 | 1.67 |  | 1.36 | 1.56 | [19 empty] | -0.3/447.4/-191.8/90/0 | 885 | 340 | [8 empty] | 14.5/-452.6/-160.8/270/0 | 835 | 250 |  |  |  | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | -549.3/168.5/-178/180/0 | 15.88 | -558.4/-237.6/-235.8/180/0 | 25 | -545/5.4/-52.3/180/0 | [6 empty] | 108420\5005300\pefy-p80_90mg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317118
26 | 108420 | 50053003220070 | PEFY-P112MG9 | ビル用マルチ 天井埋込形室内機 | 2022/9/15 |  | 08 | 108420\5005300\pefy-p112_140_160mg9_1.dxf | 108420\5005300\pefy-p112_140_160mg9_2.dxf | 108420\5005300\pefy-p112_140_160mg9_3.dxf | 108420\5005300\pefy-p112_140_160mg9_4.dxf | 108420\5005300\pefy-p112_140_160mg9_5.dxf | 108420\5005300\pefy-p112_140_160mg9_6.dxf | [5 empty] | 11.2 | 11.2 |  |  | 12.5 |  | 12.5 |  |  |  |  | 38 |  | 26.5 |  | 38 |  | 26.5 | 100 | 100 | 64 |  | 60 | 64 |  | 60 |  |  |  |  | 1195 | 900 | 380 | 63 | 1 | 200 |  |  |  | 0.2 | 0.49 | 0.55 | 0.47 | 0.53 |  |  |  |  | 2.54 | 2.89 |  | 2.43 | 2.78 | [19 empty] | 0/447.4/-191.8/90/0 | 1050 | 340 | [8 empty] | 15/-452.6/-160.8/270/0 | 1000 | 250 |  |  |  | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | -631.5/-168.5/-178/180/0 | 15.88 | -640.6/-237.6/-235.8/180/0 | 25 | -627.2/5.4/-52.3/180/0 | [6 empty] | 108420\5005300\pefy-p112_140_160mg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317119
27 | 108420 | 50053003220070 | PEFY-P140MG9 | ビル用マルチ 天井埋込形室内機 | 2022/9/15 |  | 08 | 108420\5005300\pefy-p112_140_160mg9_1.dxf | 108420\5005300\pefy-p112_140_160mg9_2.dxf | 108420\5005300\pefy-p112_140_160mg9_3.dxf | 108420\5005300\pefy-p112_140_160mg9_4.dxf | 108420\5005300\pefy-p112_140_160mg9_5.dxf | 108420\5005300\pefy-p112_140_160mg9_6.dxf | [5 empty] | 14 | 14 |  |  | 16 |  | 16 |  |  |  |  | 38 |  | 26.5 |  | 38 |  | 26.5 | 100 | 100 | 65 |  | 61 | 65 |  | 61 |  |  |  |  | 1195 | 900 | 380 | 63 | 1 | 200 |  |  |  | 0.2 | 0.49 | 0.55 | 0.47 | 0.53 |  |  |  |  | 2.54 | 2.89 |  | 2.43 | 2.78 | [19 empty] | 0/447.4/-191.8/90/0 | 1050 | 340 | [8 empty] | 15/-452.6/-160.8/270/0 | 1000 | 250 |  |  |  | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | -631.5/-168.5/-178/180/0 | 15.88 | -640.6/-237.6/-235.8/180/0 | 25 | -627.2/5.4/-52.3/180/0 | [6 empty] | 108420\5005300\pefy-p112_140_160mg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317120
28 | 108420 | 50053003220070 | PEFY-P160MG9 | ビル用マルチ 天井埋込形室内機 | 2022/9/15 |  | 08 | 108420\5005300\pefy-p112_140_160mg9_1.dxf | 108420\5005300\pefy-p112_140_160mg9_2.dxf | 108420\5005300\pefy-p112_140_160mg9_3.dxf | 108420\5005300\pefy-p112_140_160mg9_4.dxf | 108420\5005300\pefy-p112_140_160mg9_5.dxf | 108420\5005300\pefy-p112_140_160mg9_6.dxf | [5 empty] | 16 | 16 |  |  | 18 |  | 18 |  |  |  |  | 40 |  | 28 |  | 40 |  | 28 | 100 | 100 | 65 |  | 62 | 65 |  | 62 |  |  |  |  | 1195 | 900 | 380 | 65 | 1 | 200 |  |  |  | 0.23 | 0.49 | 0.55 | 0.47 | 0.53 |  |  |  |  | 2.54 | 2.89 |  | 2.43 | 2.78 | [19 empty] | 0/447.4/-191.8/90/0 | 1050 | 340 | [8 empty] | 15/-452.6/-160.8/270/0 | 1000 | 250 |  |  |  | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | -631.5/-168.5/-178/180/0 | 15.88 | -640.6/-237.6/-235.8/180/0 | 25 | -627.2/5.4/-52.3/180/0 | [6 empty] | 108420\5005300\pefy-p112_140_160mg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317121
29 | 108420 | 50053003220070 | PEFY-P224MG9 | ビル用マルチ 天井埋込形室内機 | 2022/9/15 |  | 08 | 108420\5005300\pefy-p224mg9_1.dxf | 108420\5005300\pefy-p224mg9_2.dxf | 108420\5005300\pefy-p224mg9_3.dxf | 108420\5005300\pefy-p224mg9_4.dxf | 108420\5005300\pefy-p224mg9_5.dxf | 108420\5005300\pefy-p224mg9_6.dxf | [5 empty] | 22.4 | 22.4 |  |  | 25 |  | 25 |  |  |  |  | 58 |  | 58 |  | 58 |  | 58 | 200 | 200 | 70 |  |  | 70 | [6 empty] | 1250 | 1120 | 470 | 98 | 3 | 200 |  |  |  | 0.69 | 0.92 | 1 | 0.92 | 1 |  |  |  |  | 3 | 3.3 |  | 3 | 3.3 | [19 empty] | 27/557.5/-236/90/0 | 1100 | 420 | [8 empty] | 25/-562.5/-195/270/0 | 1100 | 340 |  |  |  | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | -726.1/-189.5/-261/180/0 | 19.05 | -726.1/-284.5/-305.5/180/0 | 25 | -656.1/-111.5/-440.8/180/0 | [6 empty] | 108420\5005300\pefy-p224mg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317122
30 | 108420 | 50053003220070 | PEFY-P280MG9 | ビル用マルチ 天井埋込形室内機 | 2022/9/15 |  | 08 | 108420\5005300\pefy-p280mg9_1.dxf | 108420\5005300\pefy-p280mg9_2.dxf | 108420\5005300\pefy-p280mg9_3.dxf | 108420\5005300\pefy-p280mg9_4.dxf | 108420\5005300\pefy-p280mg9_5.dxf | 108420\5005300\pefy-p280mg9_6.dxf | [5 empty] | 28 | 28 |  |  | 31.5 |  | 31.5 |  |  |  |  | 72 |  | 72 |  | 72 |  | 72 | 200 | 200 | 75 |  |  | 75 | [6 empty] | 1250 | 1120 | 470 | 101 | 3 | 200 |  |  |  | 0.87 | 1.1 | 1.25 | 1.1 | 1.25 |  |  |  |  | 3.65 | 4.2 |  | 3.65 | 4.2 | [19 empty] | 27/557.5/-236/90/0 | 1100 | 420 | [8 empty] | 25/-562.5/-195/270/0 | 1100 | 340 |  |  |  | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | -726.1/-189.5/-261/180/0 | 22.2 | -726.1/-284.5/-305.5/180/0 | 25 | -656.1/-111.5/-440.8/180/0 | [6 empty] | 108420\5005300\pefy-p280mg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317123
39 | 108420 | 50053003220070 | PEFY-P224SMG9 | ビル用マルチ 天井埋込形室内機 | 2022/9/15 |  | 08 | 108420\5005300\pefy-p224smg9_1.dxf | 108420\5005300\pefy-p224smg9_2.dxf | 108420\5005300\pefy-p224smg9_3.dxf | 108420\5005300\pefy-p224smg9_4.dxf | 108420\5005300\pefy-p224smg9_5.dxf | 108420\5005300\pefy-p224smg9_6.dxf | [5 empty] | 22.4 | 22.4 |  |  | 25 |  | 25 |  |  |  |  | 72 | 61 | 50 |  | 72 | 61 | 50 | 150 | 150 | 67 | 66 | 65 | 67 | 66 | 65 |  |  |  |  | 1250 | 1120 | 470 | 97 | 1 | 200 |  |  |  | 0.87 | 0.68 | 0.68 | 0.68 | 0.68 |  |  |  |  | 3.95 | 3.95 |  | 3.95 | 3.95 | [19 empty] | 27/557.5/-236/90/0 | 1100 | 420 | [8 empty] | 24.6/-562.5/-190/270/0 | 1100 | 340 |  |  |  | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | -725/-189.5/-262/180/0 | 19.05 | -725/-284.5/-306/180/0 | 25 | -656/-111.5/-440/180/0 | [6 empty] | 108420\5005300\pefy-p224smg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317074
40 | 108420 | 50053003220070 | PEFY-P280SMG9 | ビル用マルチ 天井埋込形室内機 | 2022/9/15 |  | 08 | 108420\5005300\pefy-p280smg9_1.dxf | 108420\5005300\pefy-p280smg9_2.dxf | 108420\5005300\pefy-p280smg9_3.dxf | 108420\5005300\pefy-p280smg9_4.dxf | 108420\5005300\pefy-p280smg9_5.dxf | 108420\5005300\pefy-p280smg9_6.dxf | [5 empty] | 28 | 28 |  |  | 31.5 |  | 31.5 |  |  |  |  | 84 | 71 | 58 |  | 84 | 71 | 58 | 150 | 150 | 71 | 70 | 70 | 71 | 70 | 70 |  |  |  |  | 1250 | 1120 | 470 | 100 | 1 | 200 |  |  |  | 0.87 | 0.92 | 0.92 | 0.92 | 0.92 |  |  |  |  | 5.39 | 5.39 |  | 5.39 | 5.39 | [19 empty] | 27/557.5/-236/90/0 | 1100 | 420 | [8 empty] | 24.6/-562.5/-190/270/0 | 1100 | 340 |  |  |  | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | -725/-189.5/-262/180/0 | 22.2 | -725/-284.5/-306/180/0 | 25 | -656/-111.5/-440/180/0 | [6 empty] | 108420\5005300\pefy-p280smg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317075