## 108420p0
| MAKERCODE | CGRYCODE | NAME1 | NAME2 | DATE | MANUF_STOP | SPVER | FLA_FILE | FRO_FILE | REA_FILE | RIT_FILE | LEF_FILE | BOT_FILE | ETC_FILE | ASS_FLG | REF_AB&HZ50&COMP@QRT | REF_AB&HZ60&COMP@QRT | REF_AB&COMP@QRT | ACL_AB&HZ50@QKW | ACL_AB&HZ60@QKW | ACL_AB&MAX@QKW | ACL_AB&MIN@QKW | HTS_AB&HZ50@QKW | HTS_AB&HZ50&LOTMP@QKW | HTS_AB&HZ60@QKW | HTS_AB&HZ60&LOTMP@QKW | HTS_AB&MAX@QKW | HTS_AB&MIN@QKW | SA_Q&HZ50@M3M | SA_Q&HZ50&HIGH@M3M | SA_Q&HZ50&MID@M3M | SA_Q&HZ50&LOW@M3M | SA_Q&HZ60@M3M | SA_Q&HZ60&HIGH@M3M | SA_Q&HZ60&MID@M3M | SA_Q&HZ60&LOW@M3M | SP&HZ50@PA | SP&HZ60@PA | NOISE_PWL&HZ50&HIGH@DB | NOISE_PWL&HZ50&MID@DB | NOISE_PWL&HZ50&LOW@DB | NOISE_PWL&HZ60&HIGH@DB | NOISE_PWL&HZ60&MID@DB | NOISE_PWL&HZ60&LOW@DB | NOISE_PWL&ACL&HZ50@DB | NOISE_PWL&ACL&HZ60@DB | NOISE_PWL&HTS&HZ50@DB | NOISE_PWL&HTS&HZ60@DB | SIZE_W@MM | SIZE_D@MM | SIZE_H@MM | PRD_QA@WKG | PHASE@ES | VOLTAGE@EV | ELEC_OUT&HZ50&COMP@EKW | ELEC_OUT&HZ60&COMP@EKW | ELEC_OUT&COMP@EKW | ELEC_OUT&FAN@EKW | ELECONSUM&ACL&HZ50@EKW | ELECONSUM&ACL&HZ60@EKW | ELECONSUM&HTS&HZ50@EKW | ELECONSUM&HTS&HZ60@EKW | ELECONSUM&HTS&HZ50&LOTMP@EKW | ELECONSUM&HTS&HZ60&LOTMP@EKW | ELECONSUM&HZ50@EKW | ELECONSUM&HZ60@EKW | OPE_A&ACL&HZ50@EA | OPE_A&ACL&HZ60@EA | OPE_A&ACL&MAX@EA | OPE_A&HTS&HZ50@EA | OPE_A&HTS&HZ60@EA | OPE_A&HTS&MAX@EA | OPE_A&HT&HZ50@EA | OPE_A&HT&HZ60@EA | OPE_A&HZ50@EA | OPE_A&HZ50&HTER@EA | OPE_A&HZ60@EA | OPE_A&HZ60&HTER@EA | STRT_A&HZ50@EA | STRT_A&HZ60@EA | ELEC_EF&ACL&HZ50@EFF | ELEC_EF&ACL&HZ60@EFF | ELEC_EF&HTS&HZ50@EFF | ELEC_EF&HTS&HZ50&HTER@EFF | ELEC_EF&HTS&HZ60@EFF | ELEC_EF&HTS&HZ60&HTER@EFF | ELEC_EF&HT&HZ50@EFF | ELEC_EF&HT&HZ60@EFF | ELEC_EF&HZ50@EFF | ELEC_EF&HZ60@EFF | RA_CONNECT&IN&LOC@MM | RA_CONNECT&IN&SIZE_W@MM | RA_CONNECT&IN&SIZE_H@MM | SA_CONNECT&OUT&LOC&NO01@MM | SA_CONNECT&OUT&SIZE_P&NO01@MM | SA_CONNECT&OUT&LOC&NO02@MM | SA_CONNECT&OUT&SIZE_P&NO02@MM | SA_CONNECT&OUT&LOC&NO03@MM | SA_CONNECT&OUT&SIZE_P&NO03@MM | SA_CONNECT&OUT&LOC&NO04@MM | SA_CONNECT&OUT&SIZE_P&NO04@MM | SA_CONNECT&OUT&LOC&NO05@MM | SA_CONNECT&OUT&SIZE_W&NO05@MM | SA_CONNECT&OUT&SIZE_H&NO05@MM | OA_CONNECT&SIZE_P@MM | OA_CONNECT&SIZE_W@MM | OA_CONNECT&SIZE_H@MM | AIR_DBT&INDOR&ACL@THC | AIR_DBT&INDOR&HTS@THC | AIR_WBT&INDOR&ACL@THC | AIR_OST_DB&ACL@THC | AIR_OST_DB&HTS@THC | AIR_OST_DB&HTS&LOW@THC | AIR_OST_WB&ACL@THC | AIR_OST_WB&HTS@THC | AIR_OST_WB&HTS&LOW@THC | C_T&ACL&IN@THC | H_T&HTS&IN@THC | CDH_T&ACL&IN@THC | CDH_T&HTS&IN@THC | CD_T&IN@THC | CH_CONNECT&IN&LOC@MM | CH_CONNECT&OUT&LOC@MM | CD_CONNECT&IN&OUT&METH | CD_CONNECT&IN&LOC@MM | CD_CONNECT&OUT&LOC@MM | RL_CONNECT&IN&SIZE_P@MM | RL_CONNECT&IN&LOC@MM | RG_CONNECT&IN&SIZE_P@MM | RG_CONNECT&IN&LOC@MM | D_CONNECT&OUT&SIZE_P@ASIZ | D_CONNECT&OUT&LOC@MM | CH_PLS&HZ50@KPA | CH_PLS&HZ60@KPA | CDH_PLS&HZ50@KPA | CDH_PLS&HZ60@KPA | CD_PLS&HZ50@KPA | CD_PLS&HZ60@KPA | 3D_D_FILE | 製品情報
1 | 108420 | 50053003220020 | PLFY-P22LMG9 | ビル用マルチ ２方向カセット形室内機 | 2022/9/15 |  | 08 | 108420\5005300\plfy-p22_28_36_45lmg9_1.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_2.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_3.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_4.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_5.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_6.dxf | [5 empty] | 2.2 | 2.2 |  |  | 2.5 |  | 2.5 |  |  |  |  | 9.5 | 8.5 | 6.5 |  | 9.5 | 8.5 | 6.5 |  |  | 53 | 52 | 49 | 53 | 52 | 49 |  |  |  |  | 770 | 650 | 290 | 20 | 1 | 200 |  |  |  | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 |  |  |  |  | 0.3 | 0.3 |  | 0.3 | 0.3 | [36 empty] | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 6.35 | 103/-452/221.8/270/0 | 12.7 | 173/-463.4/235/270/0 | 25 | -175/-442/297/270/0 | [6 empty] | 108420\5005300\plfy-p22_28_36_45lmg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317077
2 | 108420 | 50053003220020 | PLFY-P28LMG9 | ビル用マルチ ２方向カセット形室内機 | 2022/9/15 |  | 08 | 108420\5005300\plfy-p22_28_36_45lmg9_1.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_2.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_3.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_4.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_5.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_6.dxf | [5 empty] | 2.8 | 2.8 |  |  | 3.2 |  | 3.2 |  |  |  |  | 9.5 | 8.5 | 6.5 |  | 9.5 | 8.5 | 6.5 |  |  | 53 | 52 | 49 | 53 | 52 | 49 |  |  |  |  | 770 | 650 | 290 | 20 | 1 | 200 |  |  |  | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 |  |  |  |  | 0.3 | 0.3 |  | 0.3 | 0.3 | [36 empty] | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 6.35 | 103/-452/221.8/270/0 | 12.7 | 173/-463.4/235/270/0 | 25 | -175/-442/297/270/0 | [6 empty] | 108420\5005300\plfy-p22_28_36_45lmg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317078
3 | 108420 | 50053003220020 | PLFY-P36LMG9 | ビル用マルチ ２方向カセット形室内機 | 2022/9/15 |  | 08 | 108420\5005300\plfy-p22_28_36_45lmg9_1.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_2.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_3.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_4.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_5.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_6.dxf | [5 empty] | 3.6 | 3.6 |  |  | 4 |  | 4 |  |  |  |  | 10 | 9 | 6.5 |  | 10 | 9 | 6.5 |  |  | 53 | 52 | 50 | 53 | 52 | 50 |  |  |  |  | 770 | 650 | 290 | 21 | 1 | 200 |  |  |  | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 |  |  |  |  | 0.35 | 0.35 |  | 0.35 | 0.35 | [36 empty] | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 6.35 | 103/-452/221.8/270/0 | 12.7 | 173/-463.4/235/270/0 | 25 | -175/-442/297/270/0 | [6 empty] | 108420\5005300\plfy-p22_28_36_45lmg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317079
4 | 108420 | 50053003220020 | PLFY-P45LMG9 | ビル用マルチ ２方向カセット形室内機 | 2022/9/15 |  | 08 | 108420\5005300\plfy-p22_28_36_45lmg9_1.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_2.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_3.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_4.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_5.dxf | 108420\5005300\plfy-p22_28_36_45lmg9_6.dxf | [5 empty] | 4.5 | 4.5 |  |  | 5 |  | 5 |  |  |  |  | 10.5 | 9.5 | 7 |  | 10.5 | 9.5 | 7 |  |  | 56 | 55 | 51 | 56 | 55 | 51 |  |  |  |  | 770 | 650 | 290 | 21 | 1 | 200 |  |  |  | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 |  |  |  |  | 0.45 | 0.45 |  | 0.45 | 0.45 | [36 empty] | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 6.35 | 103/-452/221.8/270/0 | 12.7 | 173/-463.4/235/270/0 | 25 | -175/-442/297/270/0 | [6 empty] | 108420\5005300\plfy-p22_28_36_45lmg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317080
5 | 108420 | 50053003220020 | PLFY-P56LMG9 | ビル用マルチ ２方向カセット形室内機 | 2022/9/15 |  | 08 | 108420\5005300\plfy-p56lmg9_1.dxf | 108420\5005300\plfy-p56lmg9_2.dxf | 108420\5005300\plfy-p56lmg9_3.dxf | 108420\5005300\plfy-p56lmg9_4.dxf | 108420\5005300\plfy-p56lmg9_5.dxf | 108420\5005300\plfy-p56lmg9_6.dxf | [5 empty] | 5.6 | 5.6 |  |  | 6.3 |  | 6.3 |  |  |  |  | 13 | 12 | 9 |  | 13 | 12 | 9 |  |  | 57 | 56 | 53 | 57 | 56 | 53 |  |  |  |  | 940 | 650 | 290 | 24 | 1 | 200 |  |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 |  |  |  |  | 0.5 | 0.5 |  | 0.5 | 0.5 | [36 empty] | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 6.35 | 103/-537/221.8/270/0 | 12.7 | 173/-548.4/235/270/0 | 25 | -175/-527/297/270/0 | [6 empty] | 108420\5005300\plfy-p56lmg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317081
6 | 108420 | 50053003220020 | PLFY-P71LMG9 | ビル用マルチ ２方向カセット形室内機 | 2022/9/15 |  | 08 | 108420\5005300\plfy-p71lmg9_1.dxf | 108420\5005300\plfy-p71lmg9_2.dxf | 108420\5005300\plfy-p71lmg9_3.dxf | 108420\5005300\plfy-p71lmg9_4.dxf | 108420\5005300\plfy-p71lmg9_5.dxf | 108420\5005300\plfy-p71lmg9_6.dxf | [5 empty] | 7.1 | 7.1 |  |  | 8 |  | 8 |  |  |  |  | 16.5 | 15 | 10.5 |  | 16.5 | 15 | 10.5 |  |  | 60 | 59 | 55 | 60 | 59 | 55 |  |  |  |  | 940 | 650 | 290 | 26 | 1 | 200 |  |  |  | 0.05 | 0.07 | 0.07 | 0.07 | 0.07 |  |  |  |  | 0.6 | 0.6 |  | 0.6 | 0.6 | [36 empty] | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | 103/-537/221.8/270/0 | 15.88 | 173/-548.4/235/270/0 | 25 | -175/-527/297/270/0 | [6 empty] | 108420\5005300\plfy-p71lmg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317082
7 | 108420 | 50053003220020 | PLFY-P80LMG9 | ビル用マルチ ２方向カセット形室内機 | 2022/9/15 |  | 08 | 108420\5005300\plfy-p80_90_112_140lmg9_1.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_2.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_3.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_4.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_5.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_6.dxf | [5 empty] | 8 | 8 |  |  | 9 |  | 9 |  |  |  |  | 19 | 16.5 | 13.5 |  | 19 | 16.5 | 13.5 |  |  | 60 | 59 | 56 | 60 | 59 | 56 |  |  |  |  | 1440 | 650 | 331 | 41 | 1 | 200 |  |  |  | 0.1 | 0.06 | 0.06 | 0.06 | 0.06 |  |  |  |  | 0.65 | 0.65 |  | 0.65 | 0.65 | [36 empty] | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | 103/-791.1/220.4/270/0 | 15.88 | 173/-802.6/235/270/0 | 25 | -175/-777/297/270/0 | [6 empty] | 108420\5005300\plfy-p80_90_112_140lmg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317083
8 | 108420 | 50053003220020 | PLFY-P90LMG9 | ビル用マルチ ２方向カセット形室内機 | 2022/9/15 |  | 08 | 108420\5005300\plfy-p80_90_112_140lmg9_1.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_2.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_3.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_4.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_5.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_6.dxf | [5 empty] | 9 | 9 |  |  | 10 |  | 10 |  |  |  |  | 22.5 | 20 | 15.5 |  | 22.5 | 20 | 15.5 |  |  | 61 | 60 | 57 | 61 | 60 | 57 |  |  |  |  | 1440 | 650 | 331 | 41 | 1 | 200 |  |  |  | 0.1 | 0.08 | 0.08 | 0.08 | 0.08 |  |  |  |  | 0.85 | 0.85 |  | 0.85 | 0.85 | [36 empty] | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | 103/-791.1/220.4/270/0 | 15.88 | 173/-802.6/235/270/0 | 25 | -175/-777/297/270/0 | [6 empty] | 108420\5005300\plfy-p80_90_112_140lmg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317084
9 | 108420 | 50053003220020 | PLFY-P112LMG9 | ビル用マルチ ２方向カセット形室内機 | 2022/9/15 |  | 08 | 108420\5005300\plfy-p80_90_112_140lmg9_1.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_2.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_3.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_4.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_5.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_6.dxf | [5 empty] | 11.2 | 11.2 |  |  | 12.5 |  | 12.5 |  |  |  |  | 26 | 23.5 | 18 |  | 26 | 23.5 | 18 |  |  | 63 | 62 | 59 | 63 | 62 | 59 |  |  |  |  | 1440 | 650 | 331 | 45 | 1 | 200 |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 1.05 | 1.05 |  | 1.05 | 1.05 | [36 empty] | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | 103/-791.1/220.4/270/0 | 15.88 | 173/-802.6/235/270/0 | 25 | -175/-777/297/270/0 | [6 empty] | 108420\5005300\plfy-p80_90_112_140lmg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317085
10 | 108420 | 50053003220020 | PLFY-P140LMG9 | ビル用マルチ ２方向カセット形室内機 | 2022/9/15 |  | 08 | 108420\5005300\plfy-p80_90_112_140lmg9_1.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_2.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_3.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_4.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_5.dxf | 108420\5005300\plfy-p80_90_112_140lmg9_6.dxf | [5 empty] | 14 | 14 |  |  | 16 |  | 16 |  |  |  |  | 31.5 | 28.5 | 23 |  | 31.5 | 28.5 | 23 |  |  | 69 | 67 | 63 | 69 | 67 | 63 |  |  |  |  | 1440 | 650 | 331 | 47 | 1 | 200 |  |  |  | 0.24 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 1.4 | 1.4 |  | 1.4 | 1.4 | [36 empty] | 27 | 20 | 19 | 35 | 7 |  |  | 6 | [11 empty] | 9.52 | 103/-791.1/220.4/270/0 | 15.88 | 173/-802.6/235/270/0 | 25 | -175/-777/297/270/0 | [6 empty] | 108420\5005300\plfy-p80_90_112_140lmg9.dwg | https://www.mitsubishielectric.co.jp/ldg/wink/ssl/displayProduct.do?pid=317090